## FC03 Read Holding Registers
Function Code | FC04 (Read Holding Registers)
No | Function | Register Address (Decimal) | Fields | Type | Accuracy | Units | Min | Max | Properties | Description
1 | Cell Voltage Difference | 0 | Cell_Difference_Disconnect | U16 | 0.001 | V | 0 | 65536 | R/W | Cell difference disconnect voltage
2 |  | 1 | Cell_Difference_Reconnect | U16 | 0.001 | V | 0 | 65536 | R/W | Cell difference reconnect voltage
3 | Cell Voltage Limit Threshold | 2 | Upper_Limit_Threshold_Cell_Voltage | U16 | 0.001 | V | 0 | 65536 | R/W | Upper Limit Threshold Cell Voltage
4 |  | 3 | Lower_Limit_Threshold_Cell_Voltage |  | 0.001 | V | 0 | 65536 | R/W | Lower Limit Threshold Cell Voltage
5 |  | 4 | Reconnect_Threshold_Cell_Voltage |  | 0.001 | V | 0 | 65536 | R/W | Reconnect Threshold Cell Voltage
6 | Temperature Limit Threshold | 5 | Upper_Limit_Threshold_Temperature_Hi | I32 | 0.001 | C | -100000 | 100000 | R/W | Upper Limit Threshold Temperature Hi Byte
7 |  | 6 | Upper_Limit_Threshold_Temperature_Lo | [5 empty] | R/W | Upper Limit Threshold Temperature Lo Byte
8 |  | 7 | Lower_Limit_Threshold_Temperature_Hi | I32 | 0.001 | C | -100000 | 100000 | R/W | Lower Limit Threshold Temperature Hi Byte
9 |  | 8 | Lower_Limit_Threshold_Temperature_Lo | [5 empty] | R/W | Lower Limit Threshold Temperature Lo Byte
10 | Save | 9 | Save into memory | U16 |  |  | 0 | 1 | R/W | Save setting into memory
11 | SSID | 10 | 1st - 2nd character | U16 |  |  |  |  | R/W | Character for ssid, write the last element with '\0' as terminated character
12 |  | 11 | 3rd - 4th character | U16 |  |  |  |  | R/W
13 |  | 12 | 5th - 6th character | U16 |  |  |  |  | R/W
14 |  | 13 | 7th - 8th character | U16 |  |  |  |  | R/W
15 |  | 14 | 9th - 10th character | U16 |  |  |  |  | R/W
16 |  | 15 | 11st - 12th character | U16 |  |  |  |  | R/W
17 |  | 16 | 13th - 14th character | U16 |  |  |  |  | R/W
18 |  | 17 | 15th - 16th character | U16 |  |  |  |  | R/W
19 | Password | 18 | 1st - 2nd character | U16 |  |  |  |  | R/W | Character for password, write the last element with '\0' as terminated character
20 |  | 19 | 3rd - 4th character | U16 |  |  |  |  | R/W
21 |  | 20 | 5th - 6th character | U16 |  |  |  |  | R/W
22 |  | 21 | 7th - 8th character | U16 |  |  |  |  | R/W
23 |  | 22 | 9th - 10th character | U16 |  |  |  |  | R/W
24 |  | 23 | 11st - 12th character | U16 |  |  |  |  | R/W
25 |  | 24 | 13th - 14th character | U16 |  |  |  |  | R/W
26 |  | 25 | 15th - 16th character | U16 |  |  |  |  | R/W
27 | IP address 1 | 26 | IP address for 1st segment | U16 |  |  | 0 | 255 | R/W | IP Address
28 | IP address 2 | 27 | IP address for 2nd segment | U16 |  |  | 0 | 255 | R/W
29 | IP address 3 | 28 | IP address for 3rd segment | U16 |  |  | 0 | 255 | R/W
30 | IP address 4 | 29 | IP address for 4th segment | U16 |  |  | 0 | 255 | R/W
31 | Gateway 1 | 30 | Gateway for 1st segment | U16 |  |  | 0 | 255 | R/W | Gateway Address
32 | Gateway 2 | 31 | Gateway for 2nd segment | U16 |  |  | 0 | 255 | R/W
33 | Gateway 3 | 32 | Gateway for 3rd segment | U16 |  |  | 0 | 255 | R/W
34 | Gateway 4 | 33 | Gateway for 4th segment | U16 |  |  | 0 | 255 | R/W
35 | Subnet 1 | 34 | Subnet for 1st segment | U16 |  |  | 0 | 255 | R/W | Subnet Address
36 | Subnet 2 | 35 | Subnet for 2nd segment | U16 |  |  | 0 | 255 | R/W
37 | Subnet 3 | 36 | Subnet for 3rd segment | U16 |  |  | 0 | 255 | R/W
38 | Subnet 4 | 37 | Subnet for 4th segment | U16 |  |  | 0 | 255 | R/W
39 | Network server type | 38 | Network server | U16 |  |  | 1 | 2 | R/W | 1 for Static, 2 for DHCP
40 | Network mode | 39 | Network mode | U16 |  |  | 1 | 2 | R/W | 1 for AP, 2 for Station
41 | Save | 40 | Save into memory | U16 |  |  | 0 | 1 | R/W | Save setting into memory

## FC04 Read Input Registers
Function Code | FC03 (Read Input Registers)
No | Function | Register Address (Decimal) | Fields | Type | Accuracy | Units | Min | Max | Properties | Description
1 | Cell Voltage Group 1 | 0 | Vcell_1 | U16 | 0.001 | V |  |  | R | Cell Voltage (Offset 1000 for next group data), e.g for Vcell_1 group 2 data is in address 0 + 1000
2 |  | 1 | Vcell_2 | U16 | 0.001 | V |  |  | R
3 |  | 2 | Vcell_3 | U16 | 0.001 | V |  |  | R
4 |  | 3 | Vcell_4 | U16 | 0.001 | V |  |  | R
5 |  | 4 | Vcell_5 | U16 | 0.001 | V |  |  | R
6 |  | 5 | Vcell_6 | U16 | 0.001 | V |  |  | R
7 |  | 6 | Vcell_7 | U16 | 0.001 | V |  |  | R
8 |  | 7 | Vcell_8 | U16 | 0.001 | V |  |  | R
9 |  | 8 | Vcell_9 | U16 | 0.001 | V |  |  | R
10 |  | 9 | Vcell_10 | U16 | 0.001 | V |  |  | R
11 |  | 10 | Vcell_11 | U16 | 0.001 | V |  |  | R
12 |  | 11 | Vcell_12 | U16 | 0.001 | V |  |  | R
13 |  | 12 | Vcell_13 | U16 | 0.001 | V |  |  | R
14 |  | 13 | Vcell_14 | U16 | 0.001 | V |  |  | R
15 |  | 14 | Vcell_15 | U16 | 0.001 | V |  |  | R
16 |  | 15 | Vcell_16 | U16 | 0.001 | V |  |  | R
17 |  | 16 | Vcell_17 | U16 | 0.001 | V |  |  | R
18 |  | 17 | Vcell_18 | U16 | 0.001 | V |  |  | R
19 |  | 18 | Vcell_19 | U16 | 0.001 | V |  |  | R
20 |  | 19 | Vcell_20 | U16 | 0.001 | V |  |  | R
21 |  | 20 | Vcell_21 | U16 | 0.001 | V |  |  | R
22 |  | 21 | Vcell_22 | U16 | 0.001 | V |  |  | R
23 |  | 22 | Vcell_23 | U16 | 0.001 | V |  |  | R
24 |  | 23 | Vcell_24 | U16 | 0.001 | V |  |  | R
25 |  | 24 | Vcell_25 | U16 | 0.001 | V |  |  | R
26 |  | 25 | Vcell_26 | U16 | 0.001 | V |  |  | R
27 |  | 26 | Vcell_27 | U16 | 0.001 | V |  |  | R
28 |  | 27 | Vcell_28 | U16 | 0.001 | V |  |  | R
29 |  | 28 | Vcell_29 | U16 | 0.001 | V |  |  | R
30 |  | 29 | Vcell_30 | U16 | 0.001 | V |  |  | R
31 |  | 30 | Vcell_31 | U16 | 0.001 | V |  |  | R
32 |  | 31 | Vcell_32 | U16 | 0.001 | V |  |  | R
33 |  | 32 | Vcell_33 | U16 | 0.001 | V |  |  | R
34 |  | 33 | Vcell_34 | U16 | 0.001 | V |  |  | R
35 |  | 34 | Vcell_35 | U16 | 0.001 | V |  |  | R
36 |  | 35 | Vcell_36 | U16 | 0.001 | V |  |  | R
37 |  | 36 | Vcell_37 | U16 | 0.001 | V |  |  | R
38 |  | 37 | Vcell_38 | U16 | 0.001 | V |  |  | R
39 |  | 38 | Vcell_39 | U16 | 0.001 | V |  |  | R
40 |  | 39 | Vcell_40 | U16 | 0.001 | V |  |  | R
41 |  | 40 | Vcell_41 | U16 | 0.001 | V |  |  | R
42 |  | 41 | Vcell_42 | U16 | 0.001 | V |  |  | R
43 |  | 42 | Vcell_43 | U16 | 0.001 | V |  |  | R
44 |  | 43 | Vcell_44 | U16 | 0.001 | V |  |  | R
45 |  | 44 | Vcell_45 | U16 | 0.001 | V |  |  | R
46 | Temperature Group 1 | 45 | Temp_1_Hi | I32 | 0.001 | C |  |  | R | Temperature (Offset 1000 for next group data), e.g for Temp_1_Hi group 2 data is in address 45 + 1000
47 |  | 46 | Temp_1_Lo
48 |  | 47 | Temp_2_Hi | I32 | 0.001 | C |  |  | R
49 |  | 48 | Temp_2_Lo
50 |  | 49 | Temp_3_Hi | I32 | 0.001 | C |  |  | R
51 |  | 50 | Temp_3_Lo
52 |  | 51 | Temp_4_Hi | I32 | 0.001 | C |  |  | R
53 |  | 52 | Temp_4_Lo
54 |  | 53 | Temp_5_Hi | I32 | 0.001 | C |  |  | R
55 |  | 54 | Temp_5_Lo
56 |  | 55 | Temp_6_Hi | I32 | 0.001 | C |  |  | R
57 |  | 56 | Temp_6_Lo
58 |  | 57 | Temp_7_Hi | I32 | 0.001 | C |  |  | R
59 |  | 58 | Temp_7_Lo
60 |  | 59 | Temp_8_Hi | I32 | 0.001 | C |  |  | R
61 |  | 60 | Temp_8_Lo
62 |  | 61 | Temp_9_Hi | I32 | 0.001 | C |  |  | R
63 |  | 62 | Temp_9_Lo
64 | Pack Voltage Group 1 | 63 | Vpack_1_Hi | U32 | 0.001 | V |  |  | R | Pack Voltage (Offset 1000 for next group data), e.g for Vpack_1_Hi group 2 data is in address 63 + 1000
65 |  | 64 | Vpack_1_Lo
66 |  | 65 | Vpack_2_Hi | U32 | 0.001 | V |  |  | R
67 |  | 66 | Vpack_2_Lo
68 |  | 67 | Vpack_3_Hi | U32 | 0.001 | V |  |  | R
69 |  | 68 | Vpack_3_Lo
70 | Pack Status | 69 | Pack_status_1 | U16 |  |  |  |  | R | bit0 : cell difference too high bit1 : cell overvoltage bit2 : cell undervoltage bit3 : overtemperature bit4 : undertemperature bit5-bit7 : reserved bit8 : wake status, 0(sleep), 1(wake) bit9 : door status 0(open), 1(close) bit10-bit15 : reserved
71 | Bid | 70 | Id | U16 |  |  |  |  | R
72 | Msg Count | 71 | Msg_Count_1 | U32 |  |  |  |  | R
73 | Frame Name | 72 | 1st - 2nd character | U16 |  |  |  |  | R | Character for frame name, write the last element with '\0' as terminated character
74 |  | 73 | 3rd - 4th character | U16 |  |  |  |  | R
75 |  | 74 | 5th - 6th character | U16 |  |  |  |  | R
76 |  | 75 | 7th - 8th character | U16 |  |  |  |  | R
77 |  | 76 | 9th - 10th character | U16 |  |  |  |  | R
78 |  | 77 | 11st - 12th character | U16 |  |  |  |  | R
79 |  | 78 | 13th - 14th character | U16 |  |  |  |  | R
80 |  | 79 | 15th - 16th character | U16 |  |  |  |  | R
81 | CMS Code | 80 | 1st - 2nd character | U16 |  |  |  |  | R | Character for cms code, write the last element with '\0' as terminated character
82 |  | 81 | 3rd - 4th character | U16 |  |  |  |  | R
83 |  | 82 | 5th - 6th character | U16 |  |  |  |  | R
84 |  | 83 | 7th - 8th character | U16 |  |  |  |  | R
85 |  | 84 | 9th - 10th character | U16 |  |  |  |  | R
86 |  | 85 | 11st - 12th character | U16 |  |  |  |  | R
87 |  | 86 | 13th - 14th character | U16 |  |  |  |  | R
88 |  | 87 | 15th - 16th character | U16 |  |  |  |  | R
89 | Base Code | 88 | 1st - 2nd character | U16 |  |  |  |  | R | Character for base code, write the last element with '\0' as terminated character
90 |  | 89 | 3rd - 4th character | U16 |  |  |  |  | R
91 |  | 90 | 5th - 6th character | U16 |  |  |  |  | R
92 |  | 91 | 7th - 8th character | U16 |  |  |  |  | R
93 |  | 92 | 9th - 10th character | U16 |  |  |  |  | R
94 |  | 93 | 11st - 12th character | U16 |  |  |  |  | R
95 |  | 94 | 13th - 14th character | U16 |  |  |  |  | R
96 |  | 95 | 15th - 16th character | U16 |  |  |  |  | R
97 | Mcu Code | 96 | 1st - 2nd character | U16 |  |  |  |  | R | Character for mcu code, write the last element with '\0' as terminated character
98 |  | 97 | 3rd - 4th character | U16 |  |  |  |  | R
99 |  | 98 | 5th - 6th character | U16 |  |  |  |  | R
100 |  | 99 | 7th - 8th character | U16 |  |  |  |  | R
101 |  | 100 | 9th - 10th character | U16 |  |  |  |  | R
102 |  | 101 | 11st - 12th character | U16 |  |  |  |  | R
103 |  | 102 | 13th - 14th character | U16 |  |  |  |  | R
104 |  | 103 | 15th - 16th character | U16 |  |  |  |  | R
105 | Site Location | 104 | 1st - 2nd character | U16 |  |  |  |  | R | Character for site location, write the last element with '\0' as terminated character
106 |  | 105 | 3rd - 4th character | U16 |  |  |  |  | R
107 |  | 106 | 5th - 6th character | U16 |  |  |  |  | R
108 |  | 107 | 7th - 8th character | U16 |  |  |  |  | R
109 |  | 108 | 9th - 10th character | U16 |  |  |  |  | R
110 |  | 109 | 11st - 12th character | U16 |  |  |  |  | R
111 |  | 110 | 13th - 14th character | U16 |  |  |  |  | R
112 |  | 111 | 15th - 16th character | U16 |  |  |  |  | R
| Connected Battery | 9000 | Conn_Pack | U16 |  |  |  |  | R | Number of connected battery
| System Status | 9001 | System bit | U16 |  |  |  |  | R | bit0 : cell difference too high bit1 : cell overvoltage bit2 : cell undervoltage bit3 : overtemperature bit4 : undertemperature bit5 : reserved bit6 : reserved bit7 : reserved bit8 : condition, 0 (standby), 1 (running) bit9 : ready to start, 0 (not ready), 1 (ready) bit10 : reserved bit11 : reserved bit12 : reserved bit13 : reserved bit14 : reserved bit15 : reserved
| Rack Sn | 9002 | 1st - 2nd character | U16 |  |  |  |  | R | Character for site location, write the last element with '\0' as terminated character
|  | 9003 | 3rd - 4th character | U16 |  |  |  |  | R
|  | 9004 | 5th - 6th character | U16 |  |  |  |  | R
|  | 9005 | 7th - 8th character | U16 |  |  |  |  | R
|  | 9006 | 9th - 10th character | U16 |  |  |  |  | R
|  | 9007 | 11st - 12th character | U16 |  |  |  |  | R
|  | 9008 | 13th - 14th character | U16 |  |  |  |  | R
|  | 9009 | 15th - 16th character | U16 |  |  |  |  | R
| MAC | 9010 | 1st MAC segment | U16 |  |  |  |  | R | MAC Address
|  | 9011 | 2nd MAC segment | U16 |  |  |  |  | R
|  | 9012 | 3rd MAC segment | U16 |  |  |  |  | R
|  | 9013 | 4th MAC segment | U16 |  |  |  |  | R
|  | 9014 | 5th MAC segment | U16 |  |  |  |  | R
|  | 9015 | 6th MAC segment | U16 |  |  |  |  | R

## FC05 Write Single Coil
Function Code | FC05 (Write Single Coil)
No | Function | Register Address (Decimal) | Fields | Type | Accuracy | Units | Min | Max | Properties | Description
1 | Addressing command | 0 | Addressing_Cmd | Bool |  |  | 0 | 1 | R/W | Addressing start command
2 | Data collection start command | 1 | Data_Collection_Start_Cmd | Bool |  |  | 0 | 1 | R/W | Data Collection start command
3 | Restart CMS | 2 | Restart_CMS_Cmd | Bool |  |  | 0 | 1 | R/W | Restart CMS
4 | Restart RMS | 3 | Restart_RMS_Cmd | Bool |  |  | 0 | 1 | R/W | Restart RMS
5 | Manual Override | 4 | Manual_override_cmd | Bool |  |  | 0 | 1 | R/W | Manual override
6 | Buzzer Output | 5 | Buzzer output state | Bool |  |  | 0 | 1 | R/W | Buzzer output state
7 | Relay Output | 6 | Relay output state | Bool |  |  | 0 | 1 | R/W | Relay output state
8 | Factory Reset | 7 | Factory_Reset_Cmd | Bool |  |  | 0 | 1 | R/W | Factory Reset
9 | Buzzer Force Output | 8 | Force_output_cmd | Bool |  |  | 0 | 1 | R/W | Force buzzer output
10 | Relay Force Output | 9 | Relay_output_cmd | Bool |  |  | 0 | 1 | R/W | Force relay output
11 | Test data collection | 10 | Test_Data_Collection_cmd | Bool |  |  | 0 | 1 | R/W | Test data collection

## Test RMS Serial
No | Name | Data | Description | Request
1 | Vcell Response | {BID:1,VCELL:[3346,3348,3347,46,3342,3346,3348,46,47,3342,3344,3347,46,45,3341,3345,3348,3345,46,3343,3351,3353,49,46,3350,3351,3352,47,47,3346,3347,3347,3348,45,3345,3346,3348,3349,45,3342,3350,3347,3348,44,3344]}\n | Normal | {BID:1,VCELL:1}\n
2 |  | {BID:1,VCELL:[3346,3348,3347,46,3342,3346,3348,46,47,3342,3044,3347,46,45,3341,3345,3348,3345,46,3343,3351,3353,49,46,3350,3351,3352,47,47,3346,3347,3347,3348,45,3345,3346,3348,3349,45,3342,3350,3347,3348,44,3344]}\n | Difference >= 304
3 |  | {BID:1,VCELL:[3346,3348,3347,46,3342,3346,3348,46,47,3342,3104,3347,46,45,3341,3345,3348,3345,46,3343,3351,3353,49,46,3350,3351,3352,47,47,3346,3347,3347,3348,45,3345,3346,3348,3349,45,3342,3350,3347,3348,44,3344]}\n | Difference >= 244
4 |  | {BID:1,VCELL:[3146,3148,3147,46,3142,3146,3148,46,47,3142,3104,3147,46,45,3141,3145,3148,3145,46,3143,3151,3153,49,46,3150,3151,3152,47,47,3146,3147,3147,3148,45,3145,3146,3148,3149,45,3142,3150,3147,3148,44,2944]}\n | Undervoltage
5 |  | {BID:1,VCELL:[3646,3648,3647,46,3642,3646,3648,46,47,3642,3604,3647,46,45,3641,3645,3648,3645,46,3643,3651,3653,49,46,3650,3651,3652,47,47,3646,3647,3647,3648,45,3645,3646,3648,3649,45,3642,3650,3647,3848,44,3644]}\n | Overvoltage
6 |  | {BID:1,VCELL:[3146,3148,3147,46,3142,3146,3148,46,47,3142,3104,3147,46,45,3141,3145,3148,3145,46,3143,3151,3153,49,46,3150,3151,3152,47,47,3146,3147,3147,3148,45,3145,3146,3148,3149,45,3142,3150,3147,3148,44,2844]}\n | Undervoltage + Diff
7 |  | {BID:1,VCELL:[3646,3648,3647,46,3642,3646,3648,46,47,3642,3604,3647,46,45,3641,3645,3648,3645,46,3643,3651,3653,49,46,3650,3651,3652,47,47,3646,3647,3647,3648,45,3645,3646,3648,3649,45,3642,3650,3647,3948,44,3644]}\n | Overvoltage + Diff
8 |  | {BID:1,VCELL:[4046,3148,3147,46,3142,3146,3148,46,47,3142,3104,3147,46,45,3141,3145,3148,3145,46,3143,3151,3153,49,46,3150,3151,3152,47,47,3146,3147,3147,3148,45,3145,3146,3148,3149,45,3142,3150,3147,3148,44,2844]}\n | Overvoltage + Undervoltage + Diff
9 | Temperature Response | {BID:1,TEMP:[29.5,29.5,32.8,29.5,29.5,32.8,29.5,29.5,32.8]}\n | Normal | {BID:1,TEMP:1}\n
10 |  | {BID:1,TEMP:[10.0,29.5,32.8,29.5,29.5,32.8,29.5,29.5,32.8]}\n | Undertemperature
11 |  | {BID:1,TEMP:[120.5,29.5,32.8,29.5,29.5,32.8,29.5,29.5,32.8]}\n | Overtemperature
12 |  | {BID:1,TEMP:[120.5,29.5,32.8,29.5,29.5,32.8,29.5,29.5,10.8]}\n | Overtemperature + Undertemperature
| Vpack Response | {BID:1,VPACK:[106793,33358,33332,40103]}\n |  | {BID:1,VPACK:1}\n
13 | CMS Status Response | {BID:1,WAKE_STATUS:1,DOOR_STATUS:0}\n | Wake + Door open | {BID:1,INFO:1}\n
14 |  | {BID:1,WAKE_STATUS:0,DOOR_STATUS:1}\n | Sleep + Door close
15 |  | {BID:1,WAKE_STATUS:1,DOOR_STATUS:1}\n | Wake + Door close
16 |  | {BID:1,WAKE_STATUS:0,DOOR_STATUS:0}\n | Sleep + Door open